ANNUAL TOWER INSPECTION REPORT

Wisconsin Department of Transportation

SP4599     9/2007

| Tower Site Name | Date Inspected |
| --- | --- |

BULB REPLACEMENT shall be performed for every incandescent beacon and obstruction lamp for each tower.  Replacement shall be performed in conjunction with the tower and lighting inspection.  Strobes and LED lighting shall only be replaced as needed.  Contractor shall use only new, high-grade bulbs with Pyrex glass, long life, 130 volt rating.  No reimbursement will be made to Contractor for bulbs installed during the bulb change.

Indicate quantity and type of lamp (incandescent, LED or strobe) used on each tower.

| Beacon – Quantity and Type | Obstruction – Quantity and Type |
| --- | --- |

TEST TOWER LIGHTING CONTROLLER AND ALARM SYSTEMS

| Satisfactory | Unsatisfactory |  |
| --- | --- | --- |
|  |  | Darken photocell to verify night-mode lighting activation |
|  |  | Proper flashing or strobe of beacons and steady illumination of all obstruction lights |
|  |  | Daytime lighting is functioning properly, where applicable |
|  |  | Alarm system detects failure of tower lighting, as applicable at each tower site |

| Lighting Controller Model Number | Controller Serial Number |
| --- | --- |

ELECTRICAL AND LIGHTING INSPECTIONS

| Satisfactory | Unsatisfactory |  |
| --- | --- | --- |
|  |  | Proper functioning of photocell |
|  |  | Proper functioning of flasher |
|  |  | Proper functioning of ALL bulbs after replacement |
|  |  | Inspect for damaged red obstruction lens |
|  |  | Inspect for damaged ruby liner and clear glass lens in beacon |
|  |  | Functioning of strobe light, if applicable |
|  |  | All strobe lights are working |
|  |  | Tower lighting electrical system |
|  |  | Junction box wiring and bulb sockets at all points above the photocell, specifically: |
|  |  | Tightness of electrical screw terminals – Tighten loose connections |
|  |  | Deterioration of insulation of electrical wiring |
|  |  | Evidence of overheating of electrical wiring |
|  |  | Bulb sockets condition – Number of sockets replaced: |

Inspect and record incandescent lamp voltage at all sockets under load.

|  | Socket 1 | Socket 2 | Socket 3 |
| --- | --- | --- | --- |
| Level 1 |  |  |  |
| Level 2 |  |  |  |
| Level 3 |  |  |  |
| Level 4 |  |  |  |

TOWER INSPECTION

| Satisfactory | Unsatisfactory |  |  |  |
| --- | --- | --- | --- | --- |
|  |  | Attachment and physical condition of antennas and transmission lines |  |  |
|  |  | Site deterioration or vandalism |  |  |
|  |  | Proper conduit attachment - Repair or replace defective conduit attachments |  |  |
|  |  | Paint fading to be checked with the In-service Aviation Orange Color Tolerance Chart |  |  |
|  |  | Paint Good | Paint OK | Needs Painting |
|  |  | Guy anchor condition and integrity including turnbuckles, wire rope clamps and nuts and safety cable through all turnbuckles; Inspect for sagging, rust and grounding |  |  |
|  |  | Guy attachments to tower |  |  |

- Tighten loose bolts and replace missing hardware on tower and attachments.

- Tighten loose bolts and replace missing hardware on guys and anchors.

- Replace missing or damaged safety cable through turnbuckles.

GUY WIRE TENSION - Inspect and provide guy tension measurement data for each applicable site.  Direct Method of measuring guy wire tension should be used.

| Tension Meter Serial Number | Air Temperature | Cable Size |
| --- | --- | --- |

| GUY LEVEL | Proper Tension |  |  | Measured Tension |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Bottom to top | Leg 1 | Leg 2 | Leg 3 | Leg 1 | Leg 2 | Leg 3 |
| 1 |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |
| 3 |  |  |  |  |  |  |
| 4 |  |  |  |  |  |  |
| 5 |  |  |  |  |  |  |

Note:  If the tower is plumb and readings are normal on one leg, no further measurements are necessary.

EXPLANATION OF UNSATISFACTORY CONDITIONS

| Specification Section | Description of Condition and Action Taken |
| --- | --- |

Continue on next page as needed